## 1. COVER
LESTRAL CONSTRUCTORA Electromecánica del Pacífico (EMP)
INDUSTRIAL TURNKEY PROJECTS • ENGINEERING + CONSTRUCTION + INSTALLATION
TURNKEY CONSTRUCTION PROPOSAL CLEANROOM WORKSHOP RENOVATION
QMX Mexico Workshop Renovation Project • Baja California, Mexico
CLIENT | QMX / QIUSHI
PROJECT | Mexico Cleanroom Workshop Renovation Project
SITE | Baja California, Mexico
BASIS OF QUOTATION | Executive project and bill of quantities dated 10-Sep-2026 (Shanghai Jingdian IFC drawing set)
QUOTATION No. | EMP-QMX-2026-09-CR • Rev. D
DATE | 10 September 2026
VALIDITY | 30 calendar days
CURRENCY | US Dollars (USD)
CONTRACT DURATION | 24 weeks from advance payment
SUBMITTED BY | ING. RODRIGO NUÑEZ LOUBET
TOTAL TURNKEY CONSTRUCTION PRICE (VAT INCLUDED)
2369001.76
CONFIDENTIAL PROPOSAL • Prepared exclusively for QMX • Blvd. Insurgentes, Tijuana, Baja California, Mexico Single point of accountability • Engineering, procurement, construction and commissioning under one contract This document supersedes proposal EMP-QMX-2026-08-F1 Rev. C.1 in respect of the scope covered by the 10-Sep-2026 executive project.

## 2. EXECUTIVE SUMMARY
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
2. EXECUTIVE SUMMARY
Lestral Constructora / Electromecánica del Pacífico (EMP) is pleased to submit this turnkey construction proposal for the renovation of the QMX workshop in Baja California, Mexico, comprising an ISO-class controlled environment together with its supporting production, inspection, change, transfer and office areas. The proposal has been priced line by line against the executive project issued on 10 September 2026 by Shanghai Jingdian Planning & Architectural Design: architectural, structural, HVAC, plumbing, electrical, fire protection and compressed air drawing sets, together with the bill of quantities in the same package. Every quantity in this quotation is taken directly from that bill of quantities, unit by unit, so that the offer can be compared against the client's own document without re-measurement. The scope covers eight disciplines and 341 priced line items: preliminaries and construction measures; architectural, structural steel and finishes; HVAC and cleanroom air systems; electrical installations; plumbing, water supply and drainage; fire protection and fire alarm; IT, CCTV and access control; and compressed air distribution. EMP acts as a single point of accountability for engineering adaptation, procurement, construction, testing and commissioning. Two matters require the client's attention and are addressed in the Value Engineering section. First, the design specifies equipment at 380 V three-phase, which is not a distribution voltage available in Mexico; the bill of quantities resolves this with a 200 kVA step-down transformer, but re-specifying the equipment at 480/277-220 V removes the transformer entirely. Second, the fire protection design follows Chinese GB codes; Mexican authority approval and plant insurance both work from NFPA. EMP has priced the project exactly as designed, and quantified both alternatives separately so the client can decide on the merits.
COST BY DISCIPLINE
| DISCIPLINE | ITEMS | DIRECT COST (USD) | % OF DIRECT
| 01 PRELIMINARIES AND CONSTRUCTION MEASURES | 22 | 266800 | 14.88%
| 02 ARCHITECTURAL, STRUCTURE AND FINISHES | 31 | 606786.77 | 33.85%
| 03 HVAC AND CLEANROOM AIR SYSTEMS | 111 | 365367 | 20.38%
| 04 ELECTRICAL INSTALLATIONS | 63 | 275378.78 | 15.36%
| 05 PLUMBING, WATER SUPPLY AND DRAINAGE | 35 | 62252.99 | 3.473%
| 06 FIRE PROTECTION AND FIRE ALARM | 51 | 150728.24 | 8.408%
| 07 IT, CCTV AND ACCESS CONTROL | 20 | 34987.99 | 1.952%
| 08 COMPRESSED AIR DISTRIBUTION | 8 | 30317.09 | 1.691%
| TOTAL DIRECT COST | 341 | 1792618.86 | 100%
| Total price before VAT | 2193520.15
| Total price including 8% VAT | 2369001.76
| Contract duration (weeks) | 24
| Value engineering saving identified | 80869.6
| Optimized duration (weeks) | 20

## 3. SCOPE OF WORK
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
3. DETAILED SCOPE OF WORK BY SYSTEM AND DISCIPLINE
The scope below is the contractual description of the works. It corresponds item by item to the priced bill of quantities in sheet 5 and to the executive project issued 10-Sep-2026.
A. PRELIMINARIES AND CONSTRUCTION MEASURES
| ▪ | Site management, superintendence, safety officer and site administration for the full duration of the works.
| ▪ | Temporary site facilities, scaffolding, lifting and rigging, temporary utilities, small tools and site housekeeping.
| ▪ | Shop drawings, adaptation of the IFC package to Mexican codes (NOM-001-SEDE-2012, NOM-002-STPS-2010, NFPA references) and production of as-built drawings.
| ▪ | Setting out, levels and survey; sample submittals, mock-ups and laboratory testing; quality supervision under an inspection and test plan.
| ▪ | Statutory insurance and contributions, protection of finished works, daily progress reporting with photographic record.
| ▪ | Indoor air quality testing at completion and fire protection testing, verification and authority sign-off.
B. ARCHITECTURAL, STRUCTURE AND FINISHES
| ▪ | Structural steel: columns, beams, purlins, tie rods, struts, access ladders, embedded plates and high-strength bolting, shop primed and erected.
| ▪ | Cleanroom envelope in 50 mm rock wool sandwich panel with aluminium profiles and fully sealed joints, including walkable ceiling panel.
| ▪ | Lightweight block walls with cement render, dowelling, tie bars, bond beams and lintels; mesh enclosure fencing.
| ▪ | Floors: electrostatic-dissipative epoxy system with copper foil grid over epoxy mortar, standard two-component epoxy, anti-slip tile over polyurethane waterproofing.
| ▪ | Cleanroom doors (double leaf, single leaf and sliding) with complete hardware; viewing windows in tempered glazing; restroom wood-veneer doors.
| ▪ | Restroom fit-out: wall and floor tile, aluminium lay-in ceiling, marble lavatory counter, framed mirror, toilet partitions, grab rails and accessories.
| ▪ | Demolition of existing restrooms, partitions and ceilings, with floor repair matched to the adjacent finish.
C. HVAC AND CLEANROOM AIR SYSTEMS
| ▪ | Cleanroom air conditioning: high static pressure fan coil units served by a 123.5 kW outdoor condensing unit, with thermostats, refnet manifolds and complete refrigerant distribution.
| ▪ | Cleanroom outside air: direct-expansion air handling unit of 2,500 m3/h at 300 Pa external static pressure with its outdoor condensing section, motorized and manual dampers, and differential pressure gauges for the pressure cascade.
| ▪ | Non-classified area conditioning: four-way ceiling cassette multi-split indoor units served by a 33.5 kW outdoor unit, and a total heat recovery ventilator for outside air.
| ▪ | Ventilation and exhaust: inline and cabinet centrifugal fans, restroom exhaust fans, activated carbon filtration unit for process exhaust, weatherproof louvers and weather caps.
| ▪ | Galvanized sheet steel ductwork fabricated and installed to GB 50243-2016 / SMACNA equivalent leakage class, with class B1 flame-retardant elastomeric insulation and canvas flexible connectors.
| ▪ | Return air column enclosures, supports and hangers, condensate drainage in UPVC, refrigerant top-up charge and all piping accessories.
| ▪ | Automatic control system for the cleanroom HVAC: controllers, field sensors, wiring, programming and commissioning.
| ▪ | Testing, adjusting and balancing of all air systems, with documented results per zone.
D. ELECTRICAL INSTALLATIONS
| ▪ | Indoor dry-type transformer of 200 kVA, 480 V primary / 380 V secondary, with pad and connections, as specified in the executive project.
| ▪ | Eight distribution boards (1APZ, 1AL1, 1AP-KT, 2AC-KT1, 2AC-KT2, 1AC-PW1, 1AC-PW2, 1ALED) per single-line diagram, complete with breakers and terminations, plus modification of existing boards affected by the new layout.
| ▪ | Hot-dip galvanized cable tray in ladder and solid-bottom types with bonding jumpers; steel conduit systems concealed in the ceiling void.
| ▪ | Copper power cabling in low-smoke halogen-free XLPE from 3x4 mm2 to 4x150+1x70 mm2, with indoor dry-type terminations.
| ▪ | Lighting: LED flat panel luminaires surface and recessed, emergency luminaires with battery back-up, directional and exit sign luminaires.
| ▪ | Switches, safety receptacles including weatherproof types, junction boxes and all final connections.
| ▪ | Earthing and bonding: supplementary equipotential bonding boxes, galvanized flat steel earthing conductors, earthing conductors in conduit, with resistance measurement and certification.
| ▪ | Commissioning of the power distribution system below 1 kV and removal of existing electrical installations.
E. PLUMBING, WATER SUPPLY AND DRAINAGE
| ▪ | Sanitary fixtures: water closets, sensor-flush urinals, undermount lavatories with mixer faucets and mop sink.
| ▪ | Potable water distribution in PP-R from De20 to De40, concealed in ceiling void and chased in wall.
| ▪ | Sanitary drainage: internally epoxy-coated galvanized steel main of De110 and PVC branches of De110, De75 and De50, with floor drains and cleanouts.
| ▪ | Valves and specialties: brass and iron gate valves, check valves, rubber flexible joints, pressure gauge and vacuum breaker.
| ▪ | Packaged sewage lifting station with two pumps of 10 m3/h at 20 m head and control panel, plus a 3.6 m3/h sewage pump with its control panel.
| ▪ | Excavation, backfill, slab restoration and wall chasing for buried and concealed pipework, with firestop sealing at all penetrations.
| ▪ | Pressure testing, leak testing and flushing of the complete installation, and removal of existing plumbing pipework and equipment.
F. FIRE PROTECTION AND FIRE ALARM
| ▪ | Fire hydrant system: hot-dip galvanized piping in DN100 and DN65 with grooved coupling system, five indoor hydrant cabinets complete with valve, nozzle and 25 m hose, and eight fire extinguisher cabinets with two extinguishers each.
| ▪ | Sprinkler system: hot-dip galvanized piping from DN25 to DN150, 118 pendent heads of K=80, signal butterfly valve with tamper switch, water flow indicator, automatic air release and inspector's test valve.
| ▪ | Seismic bracing, supports and hangers, firestop sealing at all penetrations, and hydrostatic testing, leak testing and flushing of both wet systems.
| ▪ | Fire alarm: floor-standing annunciator and control panel, addressable photoelectric smoke detectors, audible and visual devices, speakers, manual call points, hydrant call buttons and fire telephone jacks.
| ▪ | Addressable input, output and input/output modules with bus short-circuit isolators, in fire-resistant cable and dedicated steel conduit.
| ▪ | Point-to-point verification, programming and commissioning of the complete detection and alarm system, and removal of existing fire protection installations.
G. IT, CCTV AND ACCESS CONTROL
| ▪ | CCTV: eight indoor infrared network bullet cameras of 4 MP or higher with wide dynamic range and audio input, on CAT.6 cabling in dedicated tray and conduit, integrated with the existing NVR and server.
| ▪ | Access control: seven face recognition terminals with switching power supplies, single and double door magnetic locks and request-to-exit buttons.
| ▪ | Shielded and unshielded power cabling, steel conduit systems and junction boxes for both subsystems.
| ▪ | Configuration, integration with the owner's existing server and card issuer, functional testing and commissioning.
| ▪ | Head-end equipment (server, switches, NVR and card issuer) is reused from the owner's existing installation, as stated in the executive project.
H. COMPRESSED AIR DISTRIBUTION
| ▪ | SUS304 stainless steel main header of DN50 with all fittings, supports and hangers.
| ▪ | Eight DN20 drops with manual shut-off valves pre-installed on the header for future branch connection, at 0.8 m per drop.
| ▪ | Wall penetrations with firestop sealing, pressure testing, leak testing and line purging.
| ▪ | Scope is limited to the main header and the pre-installed valves; branch piping downstream of each valve to the point of use is not included, as stated in the executive project.

## 4. EXCLUSIONS & ASSUMPTIONS
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
4. EXCLUSIONS, ASSUMPTIONS AND BASIS OF PRICE
EXCLUSIONS
| 1 | Process and production equipment, and any utility connection downstream of the pre-installed valve or terminal box left by this contract.
| 2 | Compressed air branch piping downstream of the eight pre-installed DN20 valves; air compressor, dryer, receiver and treatment train.
| 3 | Head-end low-voltage equipment: CCTV server, switches, NVR, access control server and card issuer, all reused from the owner's existing installation.
| 4 | Office furniture, workstations, lockers, cabinets, changing room lavatory counters and waste bins, as noted in the client's bill of quantities.
| 5 | Deionized, purified or process water generation, storage and distribution.
| 6 | Municipal, state and federal permits, licences and rights of way; utility company connection fees and demand charges.
| 7 | Electrical service upgrade upstream of the existing main switchboard, including utility transformer, metering and primary feeder.
| 8 | Structural reinforcement of the existing building slab, foundations or roof beyond the steelwork shown in the executive project.
| 9 | Removal, treatment or disposal of hazardous materials, asbestos or contaminated soil discovered during the works.
| 10 | Cleanroom garments, consumables, spare filters beyond the first set installed, and operator training beyond the handover session.
| 11 | Third-party certification bodies' fees where the owner elects to appoint an independent certifier.
| 12 | Import duties and customs charges on owner-supplied equipment.
ASSUMPTIONS AND BASIS OF PRICE
| 1 | All quantities are taken from the client's bill of quantities dated 10-Sep-2026 without re-measurement. Quantities are subject to verification against the IFC drawings during shop drawing production; variations are settled at the unit prices in this quotation.
| 2 | Unit prices are firm for 30 calendar days and are expressed in US dollars. Where a reference exchange rate is required for peso-denominated inputs, 17.00 MXN per USD has been used; the rate is reconsidered at contract signature.
| 3 | Prices include material, labour, equipment, tools, transport, supervision, site overheads and the contractor's warranty obligations, delivered and installed in place.
| 4 | Free, safe and continuous access to the work areas during the agreed working hours, with a clear work front and adequate laydown area inside the plant.
| 5 | Existing electrical service has sufficient spare capacity at the main switchboard to serve the new load; this is confirmed by measurement during the first two weeks and reported to the owner.
| 6 | The 380 V equipment specified in the executive project is priced as designed, together with the 200 kVA step-down transformer required to serve it.
| 7 | The fire protection system is priced as designed to GB codes. Approval by the Mexican authority and by the plant insurer is assumed to be obtained by the owner on that basis, or the NFPA alternative in the Value Engineering section is adopted.
| 8 | Building structure, slab and roof are sound and able to receive the new loads without reinforcement other than that shown in the drawings.
| 9 | Work is executed on a single day shift, Monday to Saturday. A night-shift and acceleration allowance is carried in the preliminaries and is released if 24-hour access is granted.
| 10 | VAT of 8% applies under the Northern Border Region tax incentive for Baja California.
| 11 | Changes in scope, quantity or specification are executed against a signed change order at the unit prices herein.

## 5. BOQ DETAIL
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
5. PRICED BILL OF QUANTITIES — ALL FIGURES IN USD
EDITABLE CELLS: columns E and F (material and installation unit prices), shown in blue. Everything else is formula-driven and updates automatically.
CODE | DESCRIPTION | UNIT | QTY | MATERIAL U.P. | INSTALL U.P. | TOTAL U.P. | AMOUNT
SECTION A — 01 PRELIMINARIES AND CONSTRUCTION MEASURES
A-001 | Site management: superintendent, safety officer and site administration for the full construction period | LOT | 1 | 0 | 46500 | 46500 | 46500
A-002 | Temporary site facilities: erection, use and dismantling of site office, storage, changing area and temporary services | LOT | 1 | 0 | 18500 | 18500 | 18500
A-003 | Site safety and security measures: signage, barriers, PPE, fire watch and access control | LOT | 1 | 0 | 12500 | 12500 | 12500
A-004 | Unloading, receiving, custody and internal handling of owner-supplied and contractor-supplied equipment and materials | LOT | 1 | 0 | 14000 | 14000 | 14000
A-005 | Scaffolding and elevated work platforms: erection, dismantling, rental, transport and consumables | LOT | 1 | 0 | 16500 | 16500 | 16500
A-006 | All temporary utilities consumed during construction (power, water, compressed air) | LOT | 1 | 0 | 9500 | 9500 | 9500
A-007 | Insurance for personnel and equipment: civil liability, all-risk construction, IMSS and statutory contributions | LOT | 1 | 0 | 14500 | 14500 | 14500
A-008 | Lifting, hoisting and rigging required for materials and equipment placement | LOT | 1 | 0 | 8500 | 8500 | 8500
A-009 | Shop drawings, code-compliance adaptation of the IFC package to Mexican standards (NOM-001-SEDE, NOM-002-STPS, NFPA) and as-built drawing production | LOT | 1 | 0 | 26500 | 26500 | 26500
A-010 | Secondary material handling and internal transport within the plant | LOT | 1 | 0 | 6500 | 6500 | 6500
A-011 | Project elevations, setting out, layout lines and surveying | LOT | 1 | 0 | 7500 | 7500 | 7500
A-012 | Daily progress reporting and photographic record | LOT | 1 | 0 | 4800 | 4800 | 4800
A-013 | Protection of completed works and finished surfaces until handover | LOT | 1 | 0 | 6200 | 6200 | 6200
A-014 | Material sample submittals, mock-ups and laboratory testing | LOT | 1 | 0 | 5800 | 5800 | 5800
A-015 | Quality supervision of materials and workmanship, including inspection and test plan (ITP) | LOT | 1 | 0 | 8800 | 8800 | 8800
A-016 | Night-shift and schedule acceleration allowance | LOT | 1 | 0 | 9500 | 9500 | 9500
A-017 | Small tools and minor equipment usage | LOT | 1 | 0 | 5200 | 5200 | 5200
A-018 | Site housekeeping, waste segregation, removal and authorized disposal | LOT | 1 | 0 | 11500 | 11500 | 11500
A-019 | Fees payable to government authorities during contract execution | LOT | 1 | 0 | 7500 | 7500 | 7500
A-020 | Indoor air quality testing at completion | LOT | 1 | 0 | 9800 | 9800 | 9800
A-021 | Fire protection testing, inspection and authority sign-off | LOT | 1 | 0 | 12500 | 12500 | 12500
A-022 | Design drawing sets, transmittals and signature approval records | LOT | 1 | 0 | 4200 | 4200 | 4200
A TOTAL | SUBTOTAL SECTION A — 01 PRELIMINARIES AND CONSTRUCTION MEASURES | [5 empty] | 266800
SECTION B — 02 ARCHITECTURAL, STRUCTURE AND FINISHES
B-001 | Steel columns, 200x200x6 Q235B equivalent ASTM A36/A572, including base plates, stiffeners, grade-C bolts and anchor bolts, shop primed | TON | 6.386 | 2350 | 920 | 3270 | 20882.27
B-002 | Steel beams HM244x175x7x11 and HM294x200x8x12 Q235B equivalent, including connections and shop priming | TON | 21.728 | 2280 | 880 | 3160 | 68660.48
B-003 | Steel purlins, straight and diagonal tie rods, struts and access ladders: channel, angle, rectangular tube, plate and I-beam | TON | 5.926 | 2420 | 1120 | 3540 | 20978.04
B-004 | Embedded steel plates and inserts per drawings, including derusting and anti-corrosive primer | TON | 0.99475 | 2650 | 1450 | 4100 | 4078.48
B-005 | High-strength structural bolts M20, grade 10.9, including washers and torque record | SET | 388 | 4.6 | 3.1 | 7.7 | 2987.6
B-006 | 200 mm lightweight block wall with cement mortar render, including dowelling, tie bars, bond beam, curb and lintels | M2 | 159.5 | 23.5 | 29.5 | 53 | 8453.5
B-007 | Restroom wall tile 300x600 mm set with specialty adhesive over 1.5 mm polyurethane waterproofing membrane | M2 | 200.8272 | 27 | 25 | 52 | 10443.01
B-008 | Cleanroom sandwich panel partition, 50 mm rock wool core, including aluminum profiles and full silicone sealing of joints | M2 | 1127.992 | 118 | 44 | 162 | 182734.7
B-009 | Wire mesh enclosure fence, 50 mm square tube posts at 2.5 m, mesh wire not less than 2.4 mm, including gate and floor anchoring | LM | 73.2348 | 49 | 23 | 72 | 5272.91
B-010 | Anti-slip floor tile 600x600 mm set with specialty adhesive over 1.5 mm polyurethane waterproofing membrane | M2 | 61.803 | 28.5 | 23 | 51.5 | 3182.85
B-011 | Threshold stone including adhesive, substrate preparation, levelling, chamfering and edge polishing | M2 | 1.2 | 68 | 32 | 100 | 120
B-012 | Electrostatic-dissipative (ESD) epoxy floor system: epoxy primer, epoxy mortar, ESD epoxy mortar, copper foil grid and epoxy topcoat | M2 | 646.3275 | 59 | 39 | 98 | 63340.1
B-013 | Two-component epoxy floor coating, 2 mm thickness, including substrate cleaning and preparation | M2 | 119.4165 | 33 | 22 | 55 | 6567.91
B-014 | Auxiliary materials for flooring works (sealants, tapes, transition profiles, consumables) | LOT | 1 | 4500 | 0 | 4500 | 4500
B-015 | Cleanroom ceiling in 50 mm hollow-core sandwich panel, including aluminum profiles and full sealing of joints | M2 | 805.6545 | 98 | 42 | 140 | 112791.63
B-016 | Restroom aluminum lay-in ceiling 600x600x0.8 mm, including openings, edge trim, light-gauge steel grid and all fixings | M2 | 61.803 | 35 | 19 | 54 | 3337.36
B-017 | Auxiliary materials for ceiling works (hangers, sealants, trims, consumables) | LOT | 1 | 3200 | 0 | 3200 | 3200
B-018 | Cleanroom panel double-leaf door M-01, 2000x2330 mm, complete hardware set per drawings | PC | 6 | 2850 | 460 | 3310 | 19860
B-019 | Cleanroom panel sliding door, 2000x2330 mm, complete hardware set per drawings | PC | 3 | 3600 | 560 | 4160 | 12480
B-020 | Cleanroom panel single-leaf door M-02, 1000x2330 mm, complete hardware set per drawings | PC | 3 | 1750 | 360 | 2110 | 6330
B-021 | Restroom single-leaf door M-03, 1000x2300 mm, WD-01 wood-veneer finish, including frame and hardware | PC | 3 | 630 | 185 | 815 | 2445
B-022 | Restroom single-leaf door M-04, 750x2300 mm, WD-01 wood-veneer finish, including frame and hardware | PC | 1 | 570 | 175 | 745 | 745
B-023 | Viewing window 2300x1500 mm, 6 mm tempered single glazing, flush-mounted in cleanroom panel | PC | 3 | 790 | 225 | 1015 | 3045
B-024 | Viewing window 1150x1500 mm, 6 mm tempered single glazing, flush-mounted in cleanroom panel | PC | 1 | 490 | 165 | 655 | 655
B-025 | Lavatory counter with marble top 2300x600 mm, including chamfering and edge polishing | SET | 1 | 1480 | 390 | 1870 | 1870
B-026 | Silver mirror 2300x1150 mm with 1.2 mm brushed natural stainless steel frame per drawings | SET | 1 | 640 | 190 | 830 | 830
B-027 | Prefabricated toilet partitions and urinal screens, including hardware | M2 | 33.912 | 148 | 46 | 194 | 6578.93
B-028 | Accessibility grab rail, factory-finished, installed per drawings | SET | 1 | 330 | 95 | 425 | 425
B-029 | Coat hook (single), 304 stainless steel bright finish, impact protected | PC | 6 | 23 | 9 | 32 | 192
B-030 | Toilet paper holder with shelf, reference 160x100 mm, 304 stainless steel bright finish, no exposed fixings | PC | 6 | 39 | 11 | 50 | 300
B-031 | Demolition and making good: existing restroom walls, floors and ceilings; other partition walls and ceilings; floor repair to match adjacent finish | LOT | 1 | 0 | 29500 | 29500 | 29500
B TOTAL | SUBTOTAL SECTION B — 02 ARCHITECTURAL, STRUCTURE AND FINISHES | [5 empty] | 606786.77
SECTION C — 03 HVAC AND CLEANROOM AIR SYSTEMS
C-001 | High static pressure fan coil unit, 10.0 kW cooling / 11.2 kW heating, 250 W, 1ph 220V 60Hz, with integral condensate lift pump | SET | 12 | 1180 | 270 | 1450 | 17400
C-002 | High static pressure fan coil unit, 12.5 kW cooling / 14.0 kW heating, 340 W, 1ph 220V 60Hz, with integral condensate lift pump | SET | 1 | 1420 | 295 | 1715 | 1715
C-003 | Multi-split indoor unit, 4-way ceiling cassette, 5.6 kW cooling / 6.5 kW heating, 40 W, 1ph 220V 60Hz | SET | 1 | 985 | 225 | 1210 | 1210
C-004 | Outdoor condensing unit serving the fan coil system, 123.5 kW cooling / 137.5 kW heating, 41.57 kW, 3ph 60Hz, on outdoor housekeeping pad | SET | 1 | 36500 | 4300 | 40800 | 40800
C-005 | Wall-mounted thermostat with room temperature control | PC | 14 | 148 | 46 | 194 | 2716
C-006 | Refnet branch manifold, type E-102SN | PC | 5 | 168 | 56 | 224 | 1120
C-007 | Refnet branch manifold, type E-162SN | PC | 2 | 218 | 66 | 284 | 568
C-008 | Refnet branch manifold, type E-242SN | PC | 4 | 288 | 76 | 364 | 1456
C-009 | Refnet branch manifold, type E-302SN | PC | 2 | 345 | 86 | 431 | 862
C-010 | Square ceiling diffuser 350x350 mm | PC | 12 | 63 | 29 | 92 | 1104
C-011 | Square ceiling diffuser 500x500 mm | PC | 7 | 96 | 36 | 132 | 924
C-012 | Single-deflection grille 800x300 mm | PC | 13 | 79 | 31 | 110 | 1430
C-013 | Galvanized sheet steel ductwork, gauge and leakage class per GB 50243-2016 / SMACNA equivalent | M2 | 362.8576 | 34 | 26 | 60 | 21771.46
C-014 | Duct insulation, class B1 flame-retardant elastomeric foam, 20 mm thickness | M3 | 10.7296 | 325 | 185 | 510 | 5472.1
C-015 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 9.53 mm, insulated | LM | 75.152 | 9.6 | 6.6 | 16.2 | 1217.46
C-016 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 12.7 mm, insulated | LM | 10.64 | 12.6 | 7.1 | 19.7 | 209.61
C-017 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 15.9 mm, insulated | LM | 71.8928 | 16.2 | 7.6 | 23.8 | 1711.05
C-018 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 19.05 mm, insulated | LM | 80.64 | 21 | 8.6 | 29.6 | 2386.94
C-019 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 22.2 mm, insulated | LM | 14.28 | 26 | 9.6 | 35.6 | 508.37
C-020 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 28.6 mm, insulated | LM | 27.5856 | 34 | 11 | 45 | 1241.35
C-021 | Refrigerant pipe, deoxidized phosphorous seamless copper, dia. 34.92 mm, insulated | LM | 74.816 | 46 | 13.5 | 59.5 | 4451.55
C-022 | Condensate drain pipe, UPVC, DN25, graded and supported | LM | 28.28 | 4.3 | 6.6 | 10.9 | 308.25
C-023 | Condensate drain pipe, UPVC, DN32, graded and supported | LM | 66.2144 | 5.5 | 7.1 | 12.6 | 834.3
C-024 | Condensate drain pipe, UPVC, DN40, graded and supported | LM | 11.2 | 6.9 | 7.6 | 14.5 | 162.4
C-025 | Piping fittings: elbows, tees, reducers and accessories for the cleanroom AC system | LOT | 1 | 8500 | 0 | 8500 | 8500
C-026 | Pipe insulation, class B1 flame-retardant elastomeric foam, 25 mm thickness | M3 | 2.1616 | 345 | 195 | 540 | 1167.26
C-027 | Flexible duct connector, canvas type | M2 | 15 | 43 | 19 | 62 | 930
C-028 | Refrigerant top-up charge, R-410A | KG | 132.16 | 29 | 4 | 33 | 4361.28
C-029 | Fabrication and installation of general steel supports and hangers, including derusting and painting | KG | 360.4784 | 2.7 | 2.25 | 4.95 | 1784.37
C-030 | Return air column enclosure for cleanroom, L1100 x W180 x H3000 mm, in cleanroom panel | PC | 12 | 430 | 185 | 615 | 7380
C-031 | Floor and wall chasing, core drilling and firestop sealing for the cleanroom AC system | LOT | 1 | 0 | 6800 | 6800 | 6800
C-032 | System testing, commissioning and air balancing of the cleanroom AC system | LOT | 1 | 0 | 9800 | 9800 | 9800
C-033 | Direct-expansion air handling unit, indoor section: 2500 m3/h outside air, 300 Pa ESP, 25 kW cooling / 25.8 kW heating, 1.1 kW | SET | 1 | 14500 | 2250 | 16750 | 16750
C-034 | Direct-expansion air handling unit, outdoor condensing section: 25.2 kW cooling / 28 kW heating, 5.97 kW, 3ph 60Hz, on outdoor pad | SET | 1 | 9800 | 1650 | 11450 | 11450
C-035 | Square ceiling diffuser 350x350 mm | PC | 3 | 63 | 29 | 92 | 276
C-036 | Square ceiling diffuser 150x150 mm | PC | 2 | 39 | 21 | 60 | 120
C-037 | Multi-blade volume damper 250x120 mm | PC | 2 | 73 | 27 | 100 | 200
C-038 | Multi-blade volume damper 500x200 mm | PC | 3 | 120 | 35 | 155 | 465
C-039 | Motorized damper 320x400 mm | PC | 1 | 690 | 125 | 815 | 815
C-040 | Motorized opposed-blade control damper 320x400 mm | PC | 1 | 730 | 135 | 865 | 865
C-041 | Opposed-blade control damper 630x250 mm | PC | 1 | 168 | 46 | 214 | 214
C-042 | Galvanized sheet steel ductwork for the outside air system | M2 | 95.624 | 34 | 26 | 60 | 5737.44
C-043 | Duct insulation, class B1 flame-retardant elastomeric foam, 30 mm thickness | M3 | 4.6 | 365 | 195 | 560 | 2576
C-044 | Refrigerant pipe, seamless copper, dia. 9.53 mm, insulated | LM | 79.457 | 9.6 | 6.6 | 16.2 | 1287.2
C-045 | Refrigerant pipe, seamless copper, dia. 19.05 mm, insulated | LM | 79.457 | 21 | 8.6 | 29.6 | 2351.93
C-046 | Condensate drain pipe, UPVC, DN25 | LM | 5.5 | 4.3 | 6.6 | 10.9 | 59.95
C-047 | Piping fittings for the outside air system | LOT | 1 | 3200 | 0 | 3200 | 3200
C-048 | Pipe insulation, class B1 elastomeric foam, 25 mm thickness | M3 | 0.55 | 345 | 195 | 540 | 297
C-049 | Refrigerant top-up charge, R-410A | KG | 14.608 | 29 | 4 | 33 | 482.06
C-050 | Flexible duct connector, canvas type | M2 | 1.65 | 43 | 19 | 62 | 102.3
C-051 | Steel supports and hangers for the outside air system, including derusting and painting | KG | 253.687 | 2.7 | 2.25 | 4.95 | 1255.75
C-052 | Floor and wall chasing, core drilling and firestop sealing for the outside air system | LOT | 1 | 0 | 3400 | 3400 | 3400
C-053 | System testing and commissioning of the cleanroom outside air system | LOT | 1 | 0 | 4800 | 4800 | 4800
C-054 | Differential pressure gauge for cleanroom pressure cascade monitoring | PC | 3 | 215 | 62 | 277 | 831
C-055 | Automatic control system for the cleanroom HVAC: controllers, field sensors, wiring, programming and commissioning | LOT | 1 | 34500 | 8500 | 43000 | 43000
C-056 | Multi-split indoor unit, 4-way ceiling cassette, 2.8 kW cooling / 3.3 kW heating, 20 W, 1ph 220V 60Hz | SET | 3 | 730 | 195 | 925 | 2775
C-057 | Multi-split indoor unit, 4-way ceiling cassette, 4.3 kW cooling / 4.9 kW heating, 30 W, 1ph 220V 60Hz | SET | 4 | 860 | 215 | 1075 | 4300
C-058 | Multi-split indoor unit, 4-way ceiling cassette, 5.6 kW cooling / 6.5 kW heating, 40 W, 1ph 220V 60Hz | SET | 2 | 985 | 225 | 1210 | 2420
C-059 | Multi-split outdoor unit, 33.5 kW cooling / 37.5 kW heating, 10.69 kW, 3ph 60Hz, on outdoor pad | SET | 1 | 12800 | 1950 | 14750 | 14750
C-060 | Wall-mounted thermostat | PC | 9 | 148 | 46 | 194 | 1746
C-061 | Refnet branch manifold, type E-102SN | PC | 7 | 168 | 56 | 224 | 1568
C-062 | Refnet branch manifold, type E-162SN | PC | 1 | 218 | 66 | 284 | 284
C-063 | Refrigerant pipe, seamless copper, dia. 6.4 mm, insulated | LM | 46.762 | 7.6 | 6.1 | 13.7 | 640.64
C-064 | Refrigerant pipe, seamless copper, dia. 9.53 mm, insulated | LM | 47.334 | 9.6 | 6.6 | 16.2 | 766.81
C-065 | Refrigerant pipe, seamless copper, dia. 12.7 mm, insulated | LM | 113.262 | 12.6 | 7.1 | 19.7 | 2231.26
C-066 | Refrigerant pipe, seamless copper, dia. 15.9 mm, insulated | LM | 37.027 | 16.2 | 7.6 | 23.8 | 881.24
C-067 | Refrigerant pipe, seamless copper, dia. 19.05 mm, insulated | LM | 12.307 | 21 | 8.6 | 29.6 | 364.29
C-068 | Refrigerant pipe, seamless copper, dia. 28.6 mm, insulated | LM | 49.5 | 34 | 11 | 45 | 2227.5
C-069 | Condensate drain pipe, UPVC, DN20 | LM | 38.632 | 3.7 | 6.3 | 10 | 386.32
C-070 | Condensate drain pipe, UPVC, DN25 | LM | 24.629 | 4.3 | 6.6 | 10.9 | 268.46
C-071 | Condensate drain pipe, UPVC, DN32 | LM | 16.302 | 5.5 | 7.1 | 12.6 | 205.41
C-072 | Piping fittings for the non-clean multi-split system | LOT | 1 | 4200 | 0 | 4200 | 4200
C-073 | Pipe insulation, class B1 elastomeric foam, 25 mm thickness | M3 | 1.26 | 345 | 195 | 540 | 680.4
C-074 | Refrigerant top-up charge, R-410A | KG | 39.5 | 29 | 4 | 33 | 1303.5
C-075 | Steel supports and hangers, including derusting and painting | KG | 210.69 | 2.7 | 2.25 | 4.95 | 1042.92
C-076 | Floor and wall chasing, core drilling and firestop sealing | LOT | 1 | 0 | 3200 | 3200 | 3200
C-077 | System testing and commissioning of the non-clean multi-split system | LOT | 1 | 0 | 4200 | 4200 | 4200
C-078 | Total heat recovery ventilator, 800 m3/h, 175 Pa ESP, 0.585 kW, 1ph 220V 60Hz, ceiling mounted | SET | 1 | 4650 | 880 | 5530 | 5530
C-079 | Square ceiling diffuser 150x150 mm | PC | 2 | 39 | 21 | 60 | 120
C-080 | Square ceiling diffuser 250x250 mm | PC | 1 | 53 | 25 | 78 | 78
C-081 | Square ceiling diffuser 200x200 mm | PC | 1 | 46 | 23 | 69 | 69
C-082 | Single-louver return air grille 150x150 mm | PC | 1 | 33 | 19 | 52 | 52
C-083 | Single-louver return air grille 200x200 mm | PC | 2 | 39 | 21 | 60 | 120
C-084 | Weatherproof intake louver 300x300 mm with insect screen | PC | 1 | 59 | 26 | 85 | 85
C-085 | Single-louver return air grille 800x500 mm | PC | 1 | 112 | 36 | 148 | 148
C-086 | Multi-blade volume damper 160x120 mm | PC | 1 | 59 | 23 | 82 | 82
C-087 | Multi-blade volume damper 200x120 mm | PC | 2 | 63 | 25 | 88 | 176
C-088 | Multi-blade volume damper 250x120 mm | PC | 3 | 73 | 27 | 100 | 300
C-089 | Multi-blade volume damper 250x160 mm | PC | 1 | 83 | 29 | 112 | 112
C-090 | Motorized damper 350x250 mm | PC | 1 | 630 | 120 | 750 | 750
C-091 | Motorized opposed-blade control damper 350x250 mm | PC | 1 | 690 | 130 | 820 | 820
C-092 | Galvanized sheet steel ductwork for the non-clean outside air system | M2 | 123.915 | 34 | 26 | 60 | 7434.9
C-093 | Duct insulation, class B1 elastomeric foam, 30 mm thickness | M3 | 6.982 | 365 | 195 | 560 | 3909.92
C-094 | Flexible duct connector, canvas type | M2 | 2.2 | 43 | 19 | 62 | 136.4
C-095 | Steel supports and hangers, including derusting and painting | KG | 205.193 | 2.7 | 2.25 | 4.95 | 1015.71
C-096 | Floor and wall chasing, core drilling and firestop sealing | LOT | 1 | 0 | 2800 | 2800 | 2800
C-097 | System testing and commissioning of the non-clean outside air system | LOT | 1 | 0 | 3600 | 3600 | 3600
C-098 | Inline centrifugal duct fan, 1600 m3/h, 160 Pa, 900 rpm, 0.18 kW, 3ph 60Hz | SET | 1 | 1480 | 395 | 1875 | 1875
C-099 | Cabinet centrifugal fan, 2000 m3/h, 540 Pa, 1600 rpm, 1.1 kW, 3ph 60Hz | SET | 1 | 2850 | 540 | 3390 | 3390
C-100 | Restroom exhaust fan, 210 m3/h, 190 Pa, 32 W, 1ph 220V 60Hz | SET | 7 | 168 | 68 | 236 | 1652
C-101 | Activated carbon filtration unit for process exhaust, 2000 m3/h, 90% adsorption efficiency | SET | 1 | 3950 | 640 | 4590 | 4590
C-102 | Opposed-blade control damper 400x250 mm | PC | 1 | 108 | 33 | 141 | 141
C-103 | Weatherproof exhaust louver 500x400 mm | PC | 1 | 90 | 31 | 121 | 121
C-104 | Weather cap, dia. 400 mm | PC | 1 | 74 | 29 | 103 | 103
C-105 | Galvanized sheet steel ductwork for the exhaust systems | M2 | 48.3 | 34 | 26 | 60 | 2898
C-106 | Flexible duct connector, canvas type | M2 | 2.2 | 43 | 19 | 62 | 136.4
C-107 | Steel supports and hangers, including derusting and painting | KG | 89.2 | 2.7 | 2.25 | 4.95 | 441.54
C-108 | Auxiliary materials for the ventilation systems | LOT | 1 | 3800 | 0 | 3800 | 3800
C-109 | Floor and wall chasing, core drilling and firestop sealing | LOT | 1 | 0 | 2400 | 2400 | 2400
C-110 | System testing and commissioning of the ventilation systems | LOT | 1 | 0 | 3400 | 3400 | 3400
C-111 | Removal and disposal of existing HVAC ductwork, piping and equipment | LOT | 1 | 0 | 9800 | 9800 | 9800
C TOTAL | SUBTOTAL SECTION C — 03 HVAC AND CLEANROOM AIR SYSTEMS | [5 empty] | 365367
SECTION D — 04 ELECTRICAL INSTALLATIONS
D-001 | Indoor dry-type transformer, 200 kVA, primary 3ph 480V 60Hz / secondary 380V 60Hz, aluminum windings, including pad and connections | SET | 1 | 18500 | 2900 | 21400 | 21400
D-002 | Modification and re-termination of existing distribution boards affected by the new layout | LOT | 1 | 0 | 6800 | 6800 | 6800
D-003 | Distribution board 1APZ per single-line diagram, ceiling-void mounted, including breakers and terminations | SET | 1 | 5200 | 880 | 6080 | 6080
D-004 | Distribution board 1AL1 per single-line diagram, surface wall mounted | SET | 1 | 3800 | 720 | 4520 | 4520
D-005 | Distribution board 1AP-KT per single-line diagram, surface wall mounted | SET | 1 | 4600 | 800 | 5400 | 5400
D-006 | Distribution board 2AC-KT1 per single-line diagram, surface wall mounted | SET | 1 | 3400 | 670 | 4070 | 4070
D-007 | Distribution board 2AC-KT2 per single-line diagram, surface wall mounted | SET | 1 | 3400 | 670 | 4070 | 4070
D-008 | Distribution board 1AC-PW1 per single-line diagram, surface wall mounted | SET | 1 | 3900 | 720 | 4620 | 4620
D-009 | Distribution board 1AC-PW2 per single-line diagram, surface wall mounted | SET | 1 | 3900 | 720 | 4620 | 4620
D-010 | Distribution board 1ALED per single-line diagram, surface wall mounted | SET | 1 | 2900 | 620 | 3520 | 3520
D-011 | Ladder-type cable tray, 400x100x1.5 mm, hot-dip galvanized, with bonding jumpers | LM | 212 | 47 | 23 | 70 | 14840
D-012 | Solid-bottom cable tray, 200x100x1.2 mm, hot-dip galvanized, with bonding jumpers | LM | 8.47 | 33 | 19 | 52 | 440.44
D-013 | Ladder-type cable tray, 100x50x1.0 mm, hot-dip galvanized, with bonding jumpers | LM | 41.53 | 19 | 13 | 32 | 1328.96
D-014 | Set-screw steel conduit JDG20 (EMT 3/4" equivalent), concealed in ceiling void | LM | 374.4 | 3.3 | 4.9 | 8.2 | 3070.08
D-015 | Galvanized steel conduit SC15 (RMC 1/2" equivalent), concealed in ceiling void | LM | 987.49 | 3.7 | 5.3 | 9 | 8887.41
D-016 | Galvanized steel conduit SC20 (RMC 3/4" equivalent), concealed in ceiling void | LM | 586.17 | 4.5 | 5.7 | 10.2 | 5978.93
D-017 | Galvanized steel conduit SC25 (RMC 1" equivalent), concealed in ceiling void | LM | 176.71 | 5.7 | 6.3 | 12 | 2120.52
D-018 | Galvanized steel conduit SC32 (RMC 1-1/4" equivalent), concealed in ceiling void | LM | 13.14 | 7.9 | 7.1 | 15 | 197.1
D-019 | Galvanized steel conduit SC50 (RMC 2" equivalent), concealed in ceiling void | LM | 464.53 | 12.6 | 9.6 | 22.2 | 10312.57
D-020 | Galvanized steel conduit SC100 (RMC 4" equivalent) | LM | 2.25 | 28.5 | 16.5 | 45 | 101.25
D-021 | Copper power cable, low-smoke halogen-free XLPE, 4x150+1x70 mm2 - transformer incoming feeder | LM | 50 | 119 | 23 | 142 | 7100
D-022 | Copper power cable, low-smoke halogen-free XLPE, 4x120+1x70 mm2 | LM | 175 | 99 | 21 | 120 | 21000
D-023 | Copper power cable, low-smoke halogen-free XLPE, 4x70+1x35 mm2 | LM | 84.6 | 63 | 17 | 80 | 6768
D-024 | Copper power cable, low-smoke halogen-free XLPE, 4x50+1x25 mm2 | LM | 11.9 | 47 | 15 | 62 | 737.8
D-025 | Copper power cable, low-smoke halogen-free XLPE, 5x16 mm2 | LM | 64.95 | 24.5 | 9.5 | 34 | 2208.3
D-026 | Copper power cable, low-smoke halogen-free XLPE, 3x16 mm2 | LM | 396 | 15.8 | 7.8 | 23.6 | 9345.6
D-027 | Copper power cable, low-smoke halogen-free XLPE, 5x10 mm2 | LM | 66 | 16.8 | 8.2 | 25 | 1650
D-028 | Copper power cable, low-smoke halogen-free XLPE, 5x6 mm2 | LM | 64.54 | 11.2 | 6.8 | 18 | 1161.72
D-029 | Copper power cable, low-smoke halogen-free XLPE, 5x4 mm2 | LM | 86.94 | 8.4 | 6.2 | 14.6 | 1269.32
D-030 | Copper power cable, low-smoke halogen-free XLPE, 3x4 mm2 | LM | 40.86 | 5.8 | 5.4 | 11.2 | 457.63
D-031 | Indoor dry-type cable termination, 3-core and above, cross-section up to 240 mm2, below 1 kV | PC | 8 | 70 | 44 | 114 | 912
D-032 | Indoor dry-type cable termination, 3-core and above, cross-section up to 120 mm2, below 1 kV | PC | 38 | 44 | 29 | 73 | 2774
D-033 | Indoor dry-type cable termination, 3-core and above, cross-section up to 35 mm2, below 1 kV | PC | 50 | 25 | 19 | 44 | 2200
D-034 | Conductor pulled in conduit or tray, halogen-free 2.5 mm2 (fire-rated circuits) | LM | 257.24 | 1.15 | 1.35 | 2.5 | 643.1
D-035 | Conductor pulled in conduit or tray, halogen-free 4 mm2 | LM | 241.7 | 1.7 | 1.5 | 3.2 | 773.44
D-036 | Conductor pulled in conduit or tray, halogen-free 2.5 mm2 | LM | 4283.26 | 1.1 | 1.3 | 2.4 | 10279.82
D-037 | Conductor pulled in conduit or tray, halogen-free 1.5 mm2 | LM | 79.75 | 0.85 | 1.2 | 2.05 | 163.49
D-038 | Shielded control cable in conduit or tray, 2x2.5 mm2 | LM | 275.55 | 2.4 | 1.55 | 3.95 | 1088.42
D-039 | Shielded control cable in conduit or tray, 2x1.5 mm2 | LM | 220 | 1.9 | 1.45 | 3.35 | 737
D-040 | LED flat panel luminaire, T5-LED 3x18W equivalent, surface ceiling mounted | SET | 88 | 79 | 33 | 112 | 9856
D-041 | LED flat panel luminaire 600x600 mm, recessed | SET | 13 | 59 | 27 | 86 | 1118
D-042 | LED flat panel luminaire 300x300 mm, recessed | SET | 5 | 43 | 23 | 66 | 330
D-043 | Emergency ceiling luminaire, DC36V 6W LED, surface mounted | SET | 20 | 69 | 27 | 96 | 1920
D-044 | Single-face directional sign luminaire (right), DC36V 1W LED, wall mounted | SET | 6 | 53 | 23 | 76 | 456
D-045 | Single-face directional sign luminaire (left), DC36V 1W LED, wall mounted | SET | 3 | 53 | 23 | 76 | 228
D-046 | Safety exit sign luminaire type S, DC36V 1W LED, wall mounted | SET | 3 | 59 | 25 | 84 | 252
D-047 | Exit sign luminaire type E, DC36V 1W LED, wall mounted | SET | 3 | 59 | 25 | 84 | 252
D-048 | Single-gang single-pole switch, 250V 10A, flush mounted | PC | 13 | 13 | 15 | 28 | 364
D-049 | Two-gang single-pole switch, 250V 10A, flush mounted | PC | 2 | 17 | 16 | 33 | 66
D-050 | Single-phase safety receptacle, 2-pin + 3-pin, 250V 10A, flush mounted | PC | 35 | 15 | 17 | 32 | 1120
D-051 | Single-phase safety receptacle with weatherproof cover, 250V 10A, flush mounted | PC | 3 | 23 | 19 | 42 | 126
D-052 | Steel junction box, type 86, surface mounted | PC | 385 | 4.4 | 5.7 | 10.1 | 3888.5
D-053 | Supplementary equipotential bonding box SEB, 260x150x120 mm, surface mounted | PC | 4 | 148 | 68 | 216 | 864
D-054 | Galvanized flat steel earthing conductor, 25x4 mm, concealed | LM | 44 | 6.8 | 8.8 | 15.6 | 686.4
D-055 | Earthing conductor, 4 mm2, pulled in conduit | LM | 1100 | 1.4 | 1.35 | 2.75 | 3025
D-056 | Conduit for earthing conductor, PC16, concealed | LM | 1100 | 1.65 | 2.25 | 3.9 | 4290
D-057 | Floor and wall chasing, core drilling and firestop sealing for electrical works | LOT | 1 | 0 | 8800 | 8800 | 8800
D-058 | Fabrication and installation of supports and hangers for cable tray and conduit | KG | 2433.33 | 2.7 | 2.35 | 5.05 | 12288.32
D-059 | Auxiliary materials for electrical works (connectors, lugs, tape, labels, consumables) | LOT | 1 | 12500 | 0 | 12500 | 12500
D-060 | Derusting and painting of steel supports: two coats red-lead primer, two coats grey enamel | KG | 2433.33 | 0.7 | 1.15 | 1.85 | 4501.66
D-061 | Earthing system commissioning: resistance measurement and certification to design requirement | LOT | 1 | 0 | 4500 | 4500 | 4500
D-062 | Power distribution system commissioning, AC below 1 kV (comprehensive) | LOT | 1 | 0 | 8800 | 8800 | 8800
D-063 | Removal and disposal of existing electrical conduit, wiring and equipment | LOT | 1 | 0 | 11500 | 11500 | 11500
D TOTAL | SUBTOTAL SECTION D — 04 ELECTRICAL INSTALLATIONS | [5 empty] | 275378.78
SECTION E — 05 PLUMBING, WATER SUPPLY AND DRAINAGE
E-001 | Floor-mounted water closet, complete with seat, supply and fixing set | SET | 6 | 330 | 115 | 445 | 2670
E-002 | Wall-hung urinal with sensor flush valve | SET | 2 | 495 | 135 | 630 | 1260
E-003 | Undermount lavatory with hot and cold mixer faucet | SET | 3 | 295 | 125 | 420 | 1260
E-004 | Mop sink with wall-mounted faucet | SET | 1 | 270 | 105 | 375 | 375
E-005 | PP-R potable water pipe, De40, concealed in ceiling void | LM | 11.385 | 9.8 | 8.8 | 18.6 | 211.76
E-006 | PP-R potable water pipe, De32, concealed in ceiling void | LM | 5.4219 | 7.4 | 7.8 | 15.2 | 82.41
E-007 | PP-R potable water pipe, De25, concealed in ceiling void | LM | 12.265 | 5.6 | 7 | 12.6 | 154.54
E-008 | PP-R potable water pipe, De20, concealed in ceiling void | LM | 2.64 | 4.3 | 6.4 | 10.7 | 28.25
E-009 | PP-R potable water pipe, De20, chased in wall | LM | 33 | 4.3 | 9.8 | 14.1 | 465.3
E-010 | Internally epoxy-coated galvanized steel pipe, De110, for sanitary main | LM | 78 | 43 | 23 | 66 | 5148
E-011 | PVC drainage pipe, De110 | LM | 12 | 12.8 | 11.5 | 24.3 | 291.6
E-012 | PVC drainage pipe, De75 | LM | 22.8938 | 8.8 | 9.8 | 18.6 | 425.82
E-013 | PVC drainage pipe, De50 | LM | 5.8064 | 6 | 8.2 | 14.2 | 82.45
E-014 | Piping fittings: elbows, tees, reducers and accessories for plumbing works | LOT | 1 | 5800 | 0 | 5800 | 5800
E-015 | Brass gate valve, DN32 | PC | 2 | 60 | 29 | 89 | 178
E-016 | Brass gate valve, DN25 | PC | 1 | 48 | 26 | 74 | 74
E-017 | Gate valve, DN100 | PC | 1 | 330 | 98 | 428 | 428
E-018 | Gate valve, DN50 | PC | 1 | 148 | 57 | 205 | 205
E-019 | Check valve, DN100 | PC | 1 | 350 | 98 | 448 | 448
E-020 | Check valve, DN50 | PC | 1 | 155 | 57 | 212 | 212
E-021 | Rubber flexible joint, DN100 | PC | 1 | 185 | 62 | 247 | 247
E-022 | Rubber flexible joint, DN50 | PC | 1 | 98 | 42 | 140 | 140
E-023 | Pressure gauge with isolating cock | PC | 1 | 49 | 23 | 72 | 72
E-024 | Vacuum breaker, De20 | PC | 1 | 88 | 36 | 124 | 124
E-025 | Stainless steel floor drain, DN50, with trap | PC | 4 | 64 | 39 | 103 | 412
E-026 | Cleanout, De110 | PC | 1 | 57 | 36 | 93 | 93
E-027 | Fabrication and installation of general steel supports and hangers, including derusting and painting | KG | 61.083 | 2.7 | 2.25 | 4.95 | 302.36
E-028 | Wall chasing and making good for concealed piping | LM | 33 | 8.5 | 23 | 31.5 | 1039.5
E-029 | Excavation, backfill and slab restoration for buried piping | LM | 88 | 6.5 | 27 | 33.5 | 2948
E-030 | Packaged sewage lifting station: 2 pumps, each Q=10 m3/h, H=20 m, 2.2 kW, 3ph 380V 60Hz, with control panel | SET | 1 | 12800 | 2500 | 15300 | 15300
E-031 | Sewage pump, Q=3.6 m3/h, H=20 mH2O, 0.55 kW, 3ph 380V 60Hz, with control panel | SET | 1 | 1680 | 495 | 2175 | 2175
E-032 | Floor and wall chasing, core drilling and firestop sealing for plumbing works | LOT | 1 | 0 | 3800 | 3800 | 3800
E-033 | Auxiliary materials for plumbing works (sealants, hangers, gaskets, consumables) | LOT | 1 | 4200 | 0 | 4200 | 4200
E-034 | Commissioning: pressure test, leak test and system flushing | LOT | 1 | 0 | 4800 | 4800 | 4800
E-035 | Removal and disposal of existing plumbing pipework and equipment | LOT | 1 | 0 | 6800 | 6800 | 6800
E TOTAL | SUBTOTAL SECTION E — 05 PLUMBING, WATER SUPPLY AND DRAINAGE | [5 empty] | 62252.99
SECTION F — 06 FIRE PROTECTION AND FIRE ALARM
F-001 | Hot-dip galvanized steel pipe, DN100, grooved coupling system | LM | 200 | 35 | 27 | 62 | 12400
F-002 | Hot-dip galvanized steel pipe, DN65, grooved coupling system | LM | 41.492 | 23 | 21 | 44 | 1825.65
F-003 | Piping fittings: couplings, elbows, tees and accessories for the hydrant system | LOT | 1 | 9500 | 0 | 9500 | 9500
F-004 | Indoor fire hydrant cabinet with SN65 valve, 19 mm nozzle, 25 m rubber-lined hose and DN65 gate valve | SET | 5 | 640 | 230 | 870 | 4350
F-005 | Fire extinguisher cabinet complete with two MT7 extinguishers | PC | 8 | 215 | 68 | 283 | 2264
F-006 | Butterfly valve, DN100, grooved flange connection | PC | 4 | 295 | 98 | 393 | 1572
F-007 | Butterfly valve, DN65, grooved flange connection | PC | 3 | 190 | 73 | 263 | 789
F-008 | Wall penetrations and making good for the hydrant system | LOT | 1 | 0 | 3200 | 3200 | 3200
F-009 | Fabrication and installation of steel supports and hangers, including derusting and painting | KG | 156.3353 | 2.7 | 2.35 | 5.05 | 789.49
F-010 | Floor and wall chasing, core drilling and firestop sealing | LOT | 1 | 0 | 2800 | 2800 | 2800
F-011 | Commissioning: pressure test, leak test and flushing of the hydrant system | LOT | 1 | 0 | 4500 | 4500 | 4500
F-012 | Hot-dip galvanized steel pipe, DN150, grooved coupling system | LM | 200 | 54 | 35 | 89 | 17800
F-013 | Hot-dip galvanized steel pipe, DN100, grooved coupling system | LM | 16.5 | 35 | 27 | 62 | 1023
F-014 | Hot-dip galvanized steel pipe, DN80, grooved coupling system | LM | 11 | 29 | 24 | 53 | 583
F-015 | Hot-dip galvanized steel pipe, DN65, grooved coupling system | LM | 2.64 | 23 | 21 | 44 | 116.16
F-016 | Hot-dip galvanized steel pipe, DN50, threaded system | LM | 23.595 | 17.5 | 17.5 | 35 | 825.83
F-017 | Hot-dip galvanized steel pipe, DN40, threaded system | LM | 64.603 | 14 | 15.5 | 29.5 | 1905.79
F-018 | Hot-dip galvanized steel pipe, DN32, threaded system | LM | 172.337 | 11.5 | 14 | 25.5 | 4394.59
F-019 | Hot-dip galvanized steel pipe, DN25, threaded system | LM | 142.626 | 8.8 | 12.5 | 21.3 | 3037.93
F-020 | Piping fittings: couplings, elbows, tees and accessories for the sprinkler system | LOT | 1 | 12500 | 0 | 12500 | 12500
F-021 | Pendent sprinkler head, K=80 (K5.6 equivalent), with escutcheon | PC | 118 | 23 | 27 | 50 | 5900
F-022 | Signal butterfly valve with tamper switch, DN150 | PC | 1 | 990 | 230 | 1220 | 1220
F-023 | Water flow indicator switch, DN150 | PC | 1 | 430 | 125 | 555 | 555
F-024 | Automatic air release valve, DN25 | PC | 1 | 98 | 42 | 140 | 140
F-025 | Inspector's test and drain valve, DN25 | PC | 1 | 88 | 40 | 128 | 128
F-026 | Wall penetrations and making good for the sprinkler system | LOT | 1 | 0 | 3400 | 3400 | 3400
F-027 | Fabrication and installation of steel supports, hangers and seismic bracing, including derusting and painting | KG | 568.8315 | 2.7 | 2.35 | 5.05 | 2872.6
F-028 | Floor and wall chasing, core drilling and firestop sealing | LOT | 1 | 0 | 3600 | 3600 | 3600
F-029 | Commissioning: hydrostatic test, leak test and flushing of the sprinkler system | LOT | 1 | 0 | 6800 | 6800 | 6800
F-030 | Fire alarm annunciator and control panel, floor standing | SET | 1 | 4900 | 980 | 5880 | 5880
F-031 | Bus short-circuit isolator, ceiling mounted | PC | 3 | 98 | 47 | 145 | 435
F-032 | Addressable point-type photoelectric smoke detector, ceiling mounted | PC | 21 | 70 | 44 | 114 | 2394
F-033 | Fire alarm speaker, 3 W, ceiling mounted | PC | 6 | 80 | 44 | 124 | 744
F-034 | Fire telephone jack, flush mounted | PC | 3 | 88 | 42 | 130 | 390
F-035 | Audible and visual alarm device, flush mounted | PC | 3 | 123 | 50 | 173 | 519
F-036 | Manual call point / pull station, flush mounted | PC | 3 | 80 | 42 | 122 | 366
F-037 | Fire hydrant call button, mounted inside hydrant cabinet | PC | 5 | 67 | 36 | 103 | 515
F-038 | Addressable input/output module, in module enclosure | PC | 1 | 148 | 57 | 205 | 205
F-039 | Addressable output module, in module enclosure | PC | 3 | 123 | 52 | 175 | 525
F-040 | Addressable input module, in module enclosure | PC | 5 | 118 | 50 | 168 | 840
F-041 | Fire-resistant cable in conduit or tray, 2x1.5 mm2 | LM | 425.271 | 1.6 | 1.4 | 3 | 1275.81
F-042 | Halogen-free conductor in conduit or tray, 2.5 mm2 | LM | 324.5 | 1.1 | 1.3 | 2.4 | 778.8
F-043 | Galvanized steel conduit SC20, concealed in ceiling void | LM | 263.087 | 4.5 | 5.7 | 10.2 | 2683.49
F-044 | Galvanized steel conduit SC25, concealed in ceiling void | LM | 163.581 | 5.7 | 6.3 | 12 | 1962.97
F-045 | Steel junction box, type 86, surface mounted | PC | 50 | 4.4 | 5.7 | 10.1 | 505
F-046 | Floor and wall chasing, core drilling and firestop sealing for fire alarm works | LOT | 1 | 0 | 2600 | 2600 | 2600
F-047 | Fabrication and installation of supports and hangers for tray and conduit | KG | 176.396 | 2.7 | 2.35 | 5.05 | 890.8
F-048 | Derusting and painting of steel supports: two coats primer, two coats enamel | KG | 176.396 | 0.7 | 1.15 | 1.85 | 326.33
F-049 | Fire alarm system programming, point-to-point verification and commissioning | LOT | 1 | 0 | 7800 | 7800 | 7800
F-050 | Auxiliary materials for fire alarm works (connectors, labels, terminations, consumables) | LOT | 1 | 3500 | 0 | 3500 | 3500
F-051 | Removal and disposal of existing fire protection pipework and devices | LOT | 1 | 0 | 4800 | 4800 | 4800
F TOTAL | SUBTOTAL SECTION F — 06 FIRE PROTECTION AND FIRE ALARM | [5 empty] | 150728.24
SECTION G — 07 IT, CCTV AND ACCESS CONTROL
G-001 | Indoor IR network bullet camera, 4 MP or higher, WDR, audio input, DC12V and PoE, with mounting bracket | PC | 8 | 265 | 98 | 363 | 2904
G-002 | Solid-bottom cable tray, 200x100 mm, for low-voltage systems | LM | 60 | 33 | 19 | 52 | 3120
G-003 | Category 6 network cable, CAT.6 | LM | 600 | 1.5 | 1.15 | 2.65 | 1590
G-004 | Set-screw steel conduit JDG25 (EMT 1" equivalent) | LM | 80 | 4.3 | 5.3 | 9.6 | 768
G-005 | Junction box, type 86 | PC | 8 | 4.4 | 5.7 | 10.1 | 80.8
G-006 | Wall penetrations and firestop sealing for CCTV works | LOT | 1 | 0 | 1800 | 1800 | 1800
G-007 | Fabrication and installation of steel supports and hangers, including derusting and painting | KG | 186.77 | 2.7 | 2.35 | 5.05 | 943.19
G-008 | CCTV configuration, integration with existing NVR/server and commissioning | LOT | 1 | 0 | 3400 | 3400 | 3400
G-009 | Face recognition access control terminal | PC | 7 | 640 | 150 | 790 | 5530
G-010 | Switching power supply for access control door | PC | 7 | 88 | 42 | 130 | 910
G-011 | Single-door magnetic lock, including mounting bracket | PC | 3 | 115 | 68 | 183 | 549
G-012 | Double-door magnetic lock, including mounting bracket | PC | 4 | 190 | 88 | 278 | 1112
G-013 | Request-to-exit button | PC | 7 | 34 | 29 | 63 | 441
G-014 | Shielded power cable, RVVP 6x1.0 mm2 | LM | 600 | 2.5 | 1.35 | 3.85 | 2310
G-015 | Power cable, RVV 4x1.0 mm2 | LM | 100 | 1.85 | 1.25 | 3.1 | 310
G-016 | Power cable, RVV 2x1.0 mm2 | LM | 80 | 1.15 | 1.15 | 2.3 | 184
G-017 | Set-screw steel conduit JDG20 (EMT 3/4" equivalent) | LM | 180 | 3.3 | 4.9 | 8.2 | 1476
G-018 | Set-screw steel conduit JDG25 (EMT 1" equivalent) | LM | 100 | 4.3 | 5.3 | 9.6 | 960
G-019 | Auxiliary materials for access control works | LOT | 1 | 2800 | 0 | 2800 | 2800
G-020 | Access control configuration, integration with existing server and card issuer, and commissioning | LOT | 1 | 0 | 3800 | 3800 | 3800
G TOTAL | SUBTOTAL SECTION G — 07 IT, CCTV AND ACCESS CONTROL | [5 empty] | 34987.99
SECTION H — 08 COMPRESSED AIR DISTRIBUTION
H-001 | SUS304 stainless steel compressed air pipe, DN50, main header only | LM | 150 | 59 | 35 | 94 | 14100
H-002 | SUS304 stainless steel compressed air pipe, DN20, drop to pre-installed valve (0.8 m per drop) | LM | 4 | 23 | 21 | 44 | 176
H-003 | Piping fittings: elbows, tees and accessories for the compressed air header | LOT | 1 | 6800 | 0 | 6800 | 6800
H-004 | Manual shut-off valve, DN20, pre-installed on the main header for future branch connection | PC | 8 | 98 | 47 | 145 | 1160
H-005 | Fabrication and installation of steel supports and hangers, including derusting and painting | KG | 134.8693 | 2.7 | 2.35 | 5.05 | 681.09
H-006 | Wall penetrations and firestop sealing for compressed air works | LOT | 1 | 0 | 1600 | 1600 | 1600
H-007 | Auxiliary materials for compressed air works | LOT | 1 | 2400 | 0 | 2400 | 2400
H-008 | Commissioning: pressure test, leak test and line purging | LOT | 1 | 0 | 3400 | 3400 | 3400
H TOTAL | SUBTOTAL SECTION H — 08 COMPRESSED AIR DISTRIBUTION | [5 empty] | 30317.09
TOTAL | TOTAL DIRECT COST — ALL DISCIPLINES | [5 empty] | 1792618.86

## 6. COST SUMMARY
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
6. COST SUMMARY — ALL FIGURES IN USD
| CONCEPT | RATE | AMOUNT (USD) | BASIS
| A. 01 PRELIMINARIES AND CONSTRUCTION MEASURES |  | 266800 | Sum of priced line items, sheet 5
| B. 02 ARCHITECTURAL, STRUCTURE AND FINISHES |  | 606786.77 | Sum of priced line items, sheet 5
| C. 03 HVAC AND CLEANROOM AIR SYSTEMS |  | 365367 | Sum of priced line items, sheet 5
| D. 04 ELECTRICAL INSTALLATIONS |  | 275378.78 | Sum of priced line items, sheet 5
| E. 05 PLUMBING, WATER SUPPLY AND DRAINAGE |  | 62252.99 | Sum of priced line items, sheet 5
| F. 06 FIRE PROTECTION AND FIRE ALARM |  | 150728.24 | Sum of priced line items, sheet 5
| G. 07 IT, CCTV AND ACCESS CONTROL |  | 34987.99 | Sum of priced line items, sheet 5
| H. 08 COMPRESSED AIR DISTRIBUTION |  | 30317.09 | Sum of priced line items, sheet 5
| A. TOTAL DIRECT COST |  | 1792618.86 | Material plus installation, all 341 line items, delivered and installed in place
| B. INDIRECT COST (head office overhead, bonds, financing) | 8% | 143409.51 | 8% on direct cost. Site overheads (supervision, insurance, temporary facilities, utilities) are already priced in Section A, so this rate covers head office only and avoids double counting.
| C. SUBTOTAL (direct + indirect) |  | 1936028.37
| D. CONTRACTOR'S PROFIT | 10% | 193602.84 | 10% on the subtotal above, standard for turnkey industrial work of this scale in Baja California.
| E. SUBTOTAL (direct + indirect + profit) |  | 2129631.21
| F. CONTINGENCY | 3% | 63888.94 | 3% on the subtotal above. Covers quantity variation on verification against the IFC drawings and minor unforeseen conditions in the existing building. Unused contingency is returned to the client at final account.
| G. TOTAL BEFORE VAT |  | 2193520.15 | Contract price excluding tax
| H. VAT | 8% | 175481.61 | 8% under the Northern Border Region tax incentive for Baja California
| I. TOTAL CONTRACT PRICE (VAT included) |  | 2369001.76
MATERIAL / INSTALLATION SPLIT
| Material and equipment procurement |  | 963504.3923 | Column D x column E, sheet 5
| Construction and installation works |  | 829114.4822 | Column D x column F, sheet 5

## 7. COMMERCIAL TERMS
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
7. COMMERCIAL TERMS AND CONDITIONS
7.1 PAYMENT SCHEDULE
| MILESTONE | % OF PRICE | AMOUNT (USD) | RELEASE CONDITION
| Advance payment on contract signature (week 1) | 30% | 710700.53 | Signed contract or purchase order, invoice and advance payment bond if required
| Progress estimate 1 - structure and partitions (week 7) | 20% | 473800.35 | Certified progress, invoice and photographic report
| Progress estimate 2 - MEP rough-in complete (week 13) | 25% | 592250.44 | Certified progress, invoice and rough-in inspection sign-off
| Progress estimate 3 - finishes and equipment set (week 18) | 15% | 355350.26 | Certified progress, invoice and test reports
| Final payment on handover and acceptance (week 24) | 10% | 236900.18 | Handover certificate, close-out dossier and invoice
| TOTAL | 100% | 2369001.76
7.2 OFFER VALIDITY AND CURRENCY
• Validity: 30 calendar days from 10 September 2026. After that date prices are subject to review against supplier quotations then current.
• Currency: US dollars (USD). All payments are made in USD. Where a reference exchange rate is needed for peso inputs, 17.00 MXN/USD has been used and is reconsidered at contract signature.
• Prices are unit prices, firm for the validity period, and include material, labour, equipment, tools, transport, supervision and site overheads, delivered and installed in place.
• VAT of 8% applies under the Northern Border Region tax incentive for Baja California and is shown separately in the cost summary.
7.3 ADVANCE PAYMENT AND ESTIMATES
• Advance payment: 30% of the contract price on signature, against invoice and, if required by the client, an advance payment bond issued by a Mexican surety.
• The advance is amortized proportionally against each subsequent progress estimate.
• Progress estimates are submitted monthly, certified jointly by the client's representative and EMP's superintendent, supported by measured quantities and a photographic report.
• Payment term: 7 business days from acceptance of the certified estimate and receipt of a valid invoice. Final payment: 10 business days.
• Retention: 5% of each estimate may be retained by the client and is released against the handover certificate, or may be substituted by a performance bond of equivalent value.
7.4 WARRANTIES
• Workmanship and materials: 12 months from the date of substantial completion.
• Major equipment (HVAC condensing units, air handling units, pumps, transformer, boards): 24 months, or the manufacturer's warranty where longer, transferred to the client.
• Cleanroom envelope: 12 months on panel joint integrity and pressure cascade performance, subject to the client operating the systems within the design parameters.
• Warranty response: 24 to 48 hours for critical failures affecting production; 5 business days for non-critical items.
• Warranty excludes damage from misuse, unauthorized modification, lack of scheduled maintenance, or operation outside the design conditions.
7.5 EXECUTION TIME AND PROGRAMME
• Contract duration: 24 weeks from receipt of the advance payment and the granting of site access, whichever is later.
• The programme in sheet 8 shows the critical path and the payment milestones. Long-lead equipment procurement is the governing constraint in the first ten weeks.
• Delays attributable to the client (access, decisions, owner-supplied equipment, permits) extend the programme day for day, with no cost impact for the first 15 working days in aggregate.
• Liquidated damages, if agreed, are capped at 5% of the contract price and apply only to delay attributable to EMP.
• Adoption of the Value Engineering measures in sheet 9 shortens the programme to 20 weeks, as set out in sheet 10.
7.6 QUALITY, SAFETY AND CLOSE-OUT
• Quality control under an inspection and test plan agreed with the client before mobilization, with hold points at structure, rough-in, envelope and commissioning.
• Safety management per NOM-002-STPS and the client's plant rules, with a dedicated safety officer on site throughout.
• Close-out dossier: as-built drawings, equipment manuals, warranty certificates, test and balancing reports, indoor air quality results and fire protection sign-off.
• Handover includes a training session for the client's maintenance personnel on the HVAC, controls and fire protection systems.
Respectfully submitted,
ING. RODRIGO NUÑEZ LOUBET
Lestral Constructora / Electromecánica del Pacífico (EMP) — Technical lead and single point of contact

## 8. SCHEDULE GANTT
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
8. CONSTRUCTION PROGRAMME — WEEKLY GANTT WITH CRITICAL PATH AND MILESTONES
Duration 24 weeks from advance payment. Legend: ■ critical path ■ non-critical activity ◆ milestone ▲ payment milestone
| # | ACTIVITY | PATH | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 1 | Contract award, mobilization and submittals | CP
| 2 | Long-lead equipment procurement (VRF, DX AHU, boards, transformer) | CP
| 3 | Shop drawings and NOM code-compliance adaptation | CP
| 4 | Demolition and removal of existing MEP | CP
| 5 | Wall and floor chasing, core drilling | —
| 6 | Steel structure shop fabrication | —
| 7 | Steel structure erection | CP
| 8 | Block walls and masonry | —
| 9 | HVAC ductwork rough-in | CP
| 10 | Refrigerant and condensate piping | —
| 11 | Electrical tray, conduit and wiring rough-in | —
| 12 | Sprinkler and hydrant piping | —
| 13 | Plumbing and compressed air piping | —
| 14 | Cleanroom wall panel installation | CP
| 15 | Cleanroom ceiling panel installation | CP
| 16 | HVAC equipment setting and connection | CP
| 17 | Boards, transformer and terminations | —
| 18 | Doors, viewing windows and hardware | —
| 19 | Tile, restroom finishes and partitions | —
| 20 | ESD and standard epoxy flooring | CP
| 21 | Fire alarm devices and programming | —
| 22 | Lighting, devices, CCTV and access control | —
| 23 | Pressure testing, leak testing and flushing | —
| 24 | Commissioning and air/water balancing | CP
| 25 | Cleanroom qualification and indoor air quality testing | CP
| 26 | Punch list, final cleaning, as-builts and handover | CP
PROJECT MILESTONES
| M1 Contract award and advance payment |  |  | ◆
| M2 Shop drawings approved | [5 empty] | ◆
| M3 Structure and partitions complete | [15 empty] | ◆
| M4 MEP rough-in complete | [17 empty] | ◆
| M5 Energization and equipment start-up | [20 empty] | ◆
| M6 Commissioning complete | [22 empty] | ◆
| M7 Substantial completion and handover | [25 empty] | ◆
PAYMENT MILESTONES
| Advance payment on contract signature (30%) |  |  | ▲
| Progress estimate 1 - structure and partitions (20%) | [8 empty] | ▲
| Progress estimate 2 - MEP rough-in complete (25%) | [14 empty] | ▲
| Progress estimate 3 - finishes and equipment set (15%) | [19 empty] | ▲
| Final payment on handover and acceptance (10%) | [25 empty] | ▲
Critical path: contract award and mobilization → long-lead equipment procurement → shop drawings and NOM adaptation → demolition → steel erection → HVAC ductwork rough-in → cleanroom wall panel → cleanroom ceiling panel → HVAC equipment set → epoxy flooring → commissioning and balancing → cleanroom qualification → handover. Procurement of the 123.5 kW condensing unit, the DX air handling unit and the 200 kVA transformer governs the first ten weeks; the Value Engineering measures in sheet 9 remove the transformer and the imported commodity materials from that critical path.

## 9. VALUE ENGINEERING
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
9. VALUE ENGINEERING PROPOSED BY EMP
The base quotation prices the executive project exactly as designed. The alternatives below are EMP's proposals; none has been applied to the base price. Each is quantified separately so the client can accept or reject it on its own merits. Savings are calculated on the affected line items in sheet 5.
9.1 COST REDUCTION ALTERNATIVES
| REF | ALTERNATIVE | SCHEDULE IMPACT | ESTIMATED SAVING (USD) | PERFORMANCE IMPACT
| VE-01 | Re-specify all equipment and boards at 480/277-220 V, 60 Hz (NEMA/NOM) and delete the 200 kVA 480/380 V transformer | -2 weeks | 15400 | Native NOM-001-SEDE compliance; removes ~2% transformation loss and a single point of failure; spare parts available locally instead of imported
| VE-02 | Substitute GB-standard raceway, conductor and water pipe for North American equivalents (JDG/SC to EMT/RMC, GB cable to THHN/XHHW, PP-R to CPVC) | -4 weeks | 13287.63 | Equal or better performance, UL listed and NOM certified; removes 8-12 week import lead time and customs exposure on commodity materials
| VE-03 | Convert the GB fire design to NFPA 13 / NFPA 14 hydraulic design with K5.6 heads and a single combined riser serving sprinklers and hose stations | -1 weeks | 13295.04 | Insurable design (FM/NFPA) accepted by Mexican authority and by the plant insurer; removes the re-inspection and re-work risk of a GB-only submittal
| VE-04 | Limit walkable cleanroom sandwich ceiling to classified areas; standard suspended ceiling in offices, change room and support areas | -1 weeks | 20302.49 | No effect on ISO classification: the affected areas are outside the classified envelope and carry no pressure cascade requirement
| VE-05 | Apply ESD epoxy only to the areas with a declared electrostatic requirement; standard epoxy elsewhere | neutral | 6948.02 | Requires written confirmation of the ESD zone boundary by the owner; ESD performance is unchanged inside the declared zone
| VE-06 | Use pre-insulated phenolic panel duct for the non-classified outside air and exhaust runs instead of galvanized duct with external insulation | -1 weeks | 2136.42 | Lower leakage class and better thermal performance; fabricated on site, which removes the sheet-metal shop queue from the critical path
| VE-07 | Release the night-shift and acceleration allowance in exchange for 24-hour site access and a clear work front | neutral | 9500 | Requires the owner to grant unrestricted access; if access remains restricted to a single shift, the allowance must be reinstated
| Σ | TOTAL DIRECT-COST SAVING IDENTIFIED | -4 weeks | 80869.6
9.2 PERFORMANCE ALTERNATIVES (additional capital cost, operating cost reduction)
| REF | ALTERNATIVE | ADDED CAPEX (USD) | ANNUAL OPEX SAVING (USD) | PERFORMANCE IMPACT
| VE-08 | Heat-recovery VRF bank in place of two independent condensing units | 11500 | 8600 | Transfers heat between zones that call for cooling and heating simultaneously; payback approx. 1.3 years
| VE-09 | Enthalpy recovery wheel on the 2,500 m3/h outside air unit | 6800 | 5400 | Recovers approx. 65% of the outside air enthalpy load; payback approx. 1.3 years and reduces peak demand
| VE-10 | 0-10 V dimming and occupancy control on non-classified area lighting | 0 | 3200 | No capital cost impact when specified at purchase; reduces lighting energy by approx. 35% in intermittently occupied areas
| Σ | TOTAL | 18300 | 17200
EMP's recommendation: VE-01, VE-02 and VE-03 should be treated as compliance items rather than optional savings. The 380 V distribution voltage does not exist in the Mexican grid, and the GB fire design is not the basis on which the local authority or the plant insurer will approve the installation. Adopting the three together removes the transformer, the imported commodity materials and the re-submittal risk from the critical path, and is the single largest contributor to both the cost and the schedule reduction shown in sheet 10.

## 10. BASE VS OPTIMIZED
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
10. SCENARIO COMPARISON — BASE CASE VS OPTIMIZED CASE
Base case: the executive project priced exactly as designed. Optimized case: the base case with all seven cost-reduction alternatives of sheet 9.1 adopted.
| CONCEPT | BASE CASE | OPTIMIZED CASE | DIFFERENCE
| Direct cost | 1792618.86 | 1711749.26 | -80869.6
| Indirect cost (8%) | 143409.51 | 136939.94 | -6469.57
| Profit (10%) | 193602.84 | 184868.92 | -8733.92
| Contingency (3%) | 63888.94 | 61006.74 | -2882.2
| TOTAL BEFORE VAT | 2193520.15 | 2094564.86 | -98955.29
| VAT 8% | 175481.61 | 167565.19 | -7916.42
| TOTAL CONTRACT PRICE | 2369001.76 | 2262130.05 | -106871.71
| Saving as % of contract price | 0% | 4.511% | 4.511%
| Construction duration (weeks) | 24 | 20 | -4
| Annual operating cost saving (if 9.2 adopted) | 0 | 17200 | 17200
BENEFITS OF THE OPTIMIZED CASE
• Equipment operates at a distribution voltage that exists in Mexico, so spare parts, service and future extensions are sourced locally instead of imported.
• The 200 kVA transformer disappears from the electrical room, together with its standing losses, its footprint and its 10 to 12 week lead time.
• Commodity materials (conduit, conductor, water pipe) become UL listed and NOM certified, removing the customs and lead-time exposure from the critical path.
• The fire protection system becomes insurable on an NFPA basis, which is what both the Mexican authority and the plant insurer will actually review.
• Four weeks are recovered on the critical path, which brings production start-up forward by approximately one month.
• Cleanroom classification, pressure cascade, air change rate and ESD performance inside the declared zone are unchanged in every respect.

## 11. CLIENT BOQ FORMAT
LESTRAL CONSTRUCTORA, S. DE R.L. DE C.V. ¦ ELECTROMECÁNICA DEL PACÍFICO (EMP)
11. COST SUMMARY MAPPED TO THE CLIENT'S BOQ FORMAT (sheet 01.Summary)
The same price, presented in the client's own summary structure so the two documents can be reconciled line for line.
| No. | ITEM DESCRIPTION | CONSTRUCTION AND INSTALLATION (USD) | EQUIPMENT PROCUREMENT (USD) | TOTAL COST (USD)
| 1 | Construction measures cost | 266800 | 0 | 266800
| 2 | Building decoration | 198570.566 | 408216.2105 | 606786.7765
| 3 | HVAC works | 121764.5246 | 243602.4667 | 365366.9914
| 4 | Water supply and drainage works | 26629.037 | 35623.9579 | 62252.995
| 5 | Fire protection works | 74581.9876 | 76146.2584 | 150728.2459
| 6 | Electrical works | 112676.9145 | 162701.8725 | 275378.787
| 7 | Low-voltage works | 17064.5095 | 17923.479 | 34987.9885
| 8 | Compressed air works | 11026.943 | 19290.1472 | 30317.0902
| 9 | Shipping | 0 | 0 | Included in the unit prices; no separate imported freight is carried
| 10 | Customs declaration and clearance fees | 0 | 0 | Not applicable: materials are procured domestically
| 11 | Project management fee | 400901.29 | 0 | 400901.29
| 12 | Subtotal excluding VAT | 1230015.7722 | 963504.3923 | 2193520.1645
| 13 | VAT 8% |  |  | 175481.61
| 14 | TOTAL PRICE (USD) |  |  | 2369001.7745
Line 11 carries the indirect cost, profit and contingency of sheet 6 grouped as a project management fee, which is the closest equivalent in the client's template. The total in line 14 is identical to the total contract price in sheet 6.